**FloSet®*4-Port***

**Specification Text ABV Assembly**

**PN25 rated, forged DZR FloSet® 4-Port, suitable for heating and cooling applications with water temperatures from -10°C to 120°C.**

**Handed to suit duty. Vertical or horizontal alignment. Assembly to include the FlowCon 5-position flushing by-pass incl. full isolation, on 40mm centres; FlowCon flow venturi metering station for extra low to high flow rates in the flow branch; FlowCon E-Just or Composite Automatic Balancing Valve suitable for low flow rates from 0.008 l/s in the return branch, flushing, drain & test points in the flow and return branches. Johnson Controls 4-Port with 24V Modulating or Raise Lower Actuator.**

**Valve assembly must be supplied labelled with the correct terminal unit reference, duty, flow rate, insert ID, setting, metering station ID & signal, Kv value and QR code link to technical documentation.**