FloSet®4-Port

Specification Text Commissioning Assembly

PN25 rated, forged DZR FloSet® 4-Port, suitable for heating and cooling applications with water temperatures from -10°C to 120°C.

Handed to suit duty. Vertical or horizontal alignment. Assembly to include the FlowCon 5-position flushing by-pass incl. full isolation, on 40mm centres; FlowCon Combined PT Plug & Drain in the Flow Branch; VIR FODRV in the return branch, flushing, drain & test points in the flow and return branches. Johnson Controls 4-Port with 24V Modulating or Raise Lower Actuator.

Valve assembly must be supplied labelled with the correct terminal unit reference, duty, flow rate, FODRV ID, setting, metering station ID & signal and QR code link to technical documentation.