FloSet®Contract

Specification Text

PN25 rated, forged DZR FloSet® Contract, suitable for heating and cooling applications with water temperatures from -10°C to 120°C.

Handed to suit duty. Vertical or horizontal alignment. Assembly to include the FlowCon 5-position flushing by-pass incl. full isolation, on 40mm centres, FlowCon Strainer option with integrated Test Point and Combined PT Plug & Drain in the Flow Branch, FlowCon flow venturi metering station for extra low to high flow rates in the return branch, flushing, drain & test points in the flow and return branches.

Valve assembly must be supplied labelled with the correct terminal unit reference, duty, flow rate, PICV ID, setting, metering station ID & signal and QR code link to technical documentation.