**FloSet®*Total***

**Specification Text**

**Fully BSRIA BG29/21 compliant PN25 rated, forged DZR FloSet® Total, suitable for heating and cooling applications with water temperatures from -10°C to 120°C.**

**Handed to suit duty. Vertical or horizontal alignment. Assembly to include the FlowCon 5-position flushing by-pass incl. full isolation, on 40mm centres, fitted with Automatic Air Vent, FlowCon Strainer with integrated Test Point and Combined PT Plug & Drain in the Flow Branch, FlowCon Green Pressure Independent Control Valve suitable for low flow rates from 0.005 l/s and FlowCon flow venturi metering station for extra low to high flow rates in the return branch, flushing, drain & test points in the flow and return branches and FlowCon self-calibrating full stroke IP54-rated Electric Actuator, either modulating or raise lower.**

**Valve assembly must be supplied labelled with the correct terminal unit reference, duty, flow rate, insert ID, setting, metering station ID & signal and QR code link to technical documentation.**