**FloSet****®*Mini***

**Specification Text**

**PN10 rated FloSet® Mini, suitable for heating applications with water temperatures from -10°C to 120°C.**

**Assembly to include the FlowCon 5-position flushing by-pass incl. full isolation, on 40mm centres, FlowCon flow venturi metering station for extra low to high flow rates with** **flushing, drain & test points in the flow branch and Gampper Pressure Independent Radiator Valve “Vario-DP”, suitable for low flow rates from 0.006 to 0.094 l/s and 15 to 70 kPa control range, with Afriso IP54-rated E320 KH Thermostatic Control Head (ON/OFF or 3-Point floating) with Remote Sensor in the return branch.**

**Valve assembly must be supplied labelled with the correct terminal unit reference, flow rate, setting, metering station ID & signal and QR code link to technical documentation.**